## README
La Haute Borne wind farm: asset P&L and variance analysis, 2015
Companion to github.com/syulimo/wind-performance-analysis
Purpose | Asset-management view of the same SCADA analysis: budget vs actual, variance bridge by driver, turbine ranking, reforecast.
Operating year | 2015. Budget is set ex ante from 2014 data only, so 2015 is analysed out of sample.
Budget (P50 proxy) | 2014 potential energy, long-term corrected with an ERA5 wind index (1999 to 2013), spread by the long-term monthly profile.
Revenue | Energy x tariff. The tariff on Inputs is an editable assumption; change it to see every euro figure update.
Data sources | outputs/loss_monthly.csv from the pipeline (ENGIE La Haute Borne SCADA via NREL OpenOA); ERA5 100 m wind speed from the same OpenOA dataset.
Not included | O&M, land, insurance and other costs: no public cost data exist for this site, so the P&L stops at revenue and lost revenue.
Colour legend | Blue text = hardcoded input or imported data. Black = formula. Green = direct link to another sheet. Yellow fill = assumption to edit.
How to use | Edit the yellow cells on Inputs (tariff, months of actuals). Everything else recalculates.

## Inputs
Inputs and budget
Edit yellow cells only
Item | Value | Unit | Source / note
Tariff | 82 | €/MWh | Assumption: French onshore wind feed-in tariff base level (arrêté of 17 Nov 2008, 8.2 c€/kWh), before annual indexation. Edit to test other prices or a PPA.
Months of actuals for reforecast | 6 | months | Reforecast sheet uses actuals for months 1 to this number, budget after. Enter 1 to 11.
Budget build (formulas)
2014 potential energy, fleet | 11454.794 | MWh | Expected energy from the reference power curves, 2014 (pipeline output)
Long-term / 2014 wind index ratio | 1.1643 | x | ERA5 1999 to 2013 mean over 2014; above 1 means 2014 was a low-wind year
Annual budget, P50 proxy | 13336.5216 | MWh | Spread across months by the long-term monthly profile on Wind_Index
Annual budget revenue | 1093594.7695 | €
Note on B5: Assumption, not site revenue data. Edit freely.

## Wind_Index
ERA5 wind energy index by month
Mean of min(max(ws100 - 3, 0)^3 / 9^3, 1), hourly ERA5 100 m wind speed at the site; computed in src/wpa/build_asset_pnl.py
Month | Long-term 1999-2013 | 2014 | 2015 | Budget share of year | 2015 vs long-term
Jan | 0.21619 | 0.23088 | 0.26454 | 13.66% | 22.37%
Feb | 0.19848 | 0.32558 | 0.17442 | 12.54% | -12.12%
Mar | 0.16329 | 0.074634 | 0.15919 | 10.32% | -2.512%
Apr | 0.10861 | 0.044326 | 0.092369 | 6.861% | -14.95%
May | 0.079852 | 0.11436 | 0.076558 | 5.045% | -4.125%
Jun | 0.055375 | 0.048424 | 0.049769 | 3.498% | -10.12%
Jul | 0.064838 | 0.047633 | 0.079524 | 4.096% | 22.65%
Aug | 0.052459 | 0.046732 | 0.064658 | 3.314% | 23.25%
Sep | 0.077878 | 0.0293 | 0.16815 | 4.92% | 115.9%
Oct | 0.14657 | 0.10069 | 0.055879 | 9.259% | -61.87%
Nov | 0.17062 | 0.10741 | 0.23462 | 10.78% | 37.51%
Dec | 0.24876 | 0.18961 | 0.18133 | 15.72% | -27.11%
Year | 1.5829 | 1.3596 | 1.601 |  | 1.143%

## Data_Monthly
Monthly energy by turbine (pipeline output)
Source: outputs/loss_monthly.csv, written by src/wpa/pipeline.py from 10-minute SCADA. MWh.
Turbine | Month | Actual MWh | (blank) | Potential MWh | Downtime MWh | Underperf. MWh | Icing MWh | Year | Month no. | Curtailment MWh
R80711 | 2014-01-01 | 376.238 |  | 369.831 | 0.017 | 0.57 | 0.063 | 2014 | 1 | 0
R80711 | 2014-02-01 | 502.542 |  | 499.006 | 0.263 | 0.653 | 0.031 | 2014 | 2 | 0
R80711 | 2014-03-01 | 230.081 |  | 230.849 | 0.006 | 1.463 | 0 | 2014 | 3 | 0
R80711 | 2014-04-01 | 183.188 |  | 188.032 | 0.066 | 1.142 | 0 | 2014 | 4 | 0
R80711 | 2014-05-01 | 324.149 |  | 332.228 | 0.763 | 2.272 | 0 | 2014 | 5 | 0.051
R80711 | 2014-06-01 | 202.695 |  | 220.459 | 3.554 | 3.829 | 0 | 2014 | 6 | 0.272
R80711 | 2014-07-01 | 182.274 |  | 193.604 | 0.099 | 3.938 | 0 | 2014 | 7 | 0.316
R80711 | 2014-08-01 | 195.838 |  | 204.89 | 0.051 | 2.226 | 0 | 2014 | 8 | 0
R80711 | 2014-09-01 | 143.407 |  | 153.236 | 0.007 | 3.258 | 0 | 2014 | 9 | 0
R80711 | 2014-10-01 | 209.419 |  | 210.534 | 3.437 | 0.774 | 0 | 2014 | 10 | 0.13
R80711 | 2014-11-01 | 208.921 |  | 195.371 | 1.945 | 0.441 | 0.089 | 2014 | 11 | 0
R80711 | 2014-12-01 | 392.503 |  | 396.6 | 5.036 | 1.263 | 2.497 | 2014 | 12 | 0
R80711 | 2015-01-01 | 471.024 |  | 466.427 | 0.626 | 1.898 | 0.871 | 2015 | 1 | 0
R80711 | 2015-02-01 | 341.24 |  | 320.866 | 0.51 | 1.013 | 0.295 | 2015 | 2 | 0
R80711 | 2015-03-01 | 374.639 |  | 368.267 | 0.031 | 1.12 | 0.031 | 2015 | 3 | 0
R80711 | 2015-04-01 | 266.987 |  | 266.842 | 8.768 | 1.736 | 0 | 2015 | 4 | 0
R80711 | 2015-05-01 | 271.688 |  | 270.159 | 2.684 | 1.618 | 0 | 2015 | 5 | 0
R80711 | 2015-06-01 | 210.969 |  | 210.591 | 0.081 | 2.141 | 0 | 2015 | 6 | 0
R80711 | 2015-07-01 | 225.238 |  | 277.3 | 42.219 | 3.261 | 0 | 2015 | 7 | 0.21
R80711 | 2015-08-01 | 207.165 |  | 211.422 | 0.549 | 2.592 | 0 | 2015 | 8 | 0
R80711 | 2015-09-01 | 369.845 |  | 359.419 | 0.377 | 1.366 | 0 | 2015 | 9 | 0.285
R80711 | 2015-10-01 | 177.153 |  | 168.441 | 0.296 | 1.475 | 0 | 2015 | 10 | 0
R80711 | 2015-11-01 | 465.189 |  | 458.407 | 1.551 | 1.169 | 0 | 2015 | 11 | 0.045
R80711 | 2015-12-01 | 420.789 |  | 393.668 | 0.114 | 1.431 | 0 | 2015 | 12 | 0
R80721 | 2014-01-01 | 287.035 |  | 282.547 | 0.064 | 0.207 | 0 | 2014 | 1 | 0
R80721 | 2014-02-01 | 414.165 |  | 410.836 | 0 | 0.271 | 0.032 | 2014 | 2 | 0
R80721 | 2014-03-01 | 181.649 |  | 183.546 | 0.035 | 0.777 | 0 | 2014 | 3 | 0
R80721 | 2014-04-01 | 143.017 |  | 148.773 | 0.157 | 1.629 | 0 | 2014 | 4 | 0
R80721 | 2014-05-01 | 263.633 |  | 268.996 | 4.24 | 0.611 | 0 | 2014 | 5 | 0.048
R80721 | 2014-06-01 | 157.079 |  | 173.386 | 8.236 | 2.1 | 0 | 2014 | 6 | 0.17
R80721 | 2014-07-01 | 144.689 |  | 152.596 | 0.068 | 1.666 | 0 | 2014 | 7 | 0.273
R80721 | 2014-08-01 | 151.771 |  | 159.152 | 0.037 | 1.113 | 0 | 2014 | 8 | 0
R80721 | 2014-09-01 | 108.236 |  | 113.211 | 0.073 | 1.106 | 0 | 2014 | 9 | 0
R80721 | 2014-10-01 | 162.583 |  | 164.009 | 0.056 | 1.274 | 0 | 2014 | 10 | 0.042
R80721 | 2014-11-01 | 150.112 |  | 147.369 | 1.742 | 1.23 | 0 | 2014 | 11 | 0
R80721 | 2014-12-01 | 320.002 |  | 335.534 | 9.376 | 2.358 | 2.177 | 2014 | 12 | 0
R80721 | 2015-01-01 | 374.437 |  | 381.98 | 4.778 | 2.974 | 0.728 | 2015 | 1 | 0
R80721 | 2015-02-01 | 279.724 |  | 263.54 | 0.065 | 0.834 | 0.052 | 2015 | 2 | 0
R80721 | 2015-03-01 | 241.61 |  | 238.354 | 0.215 | 0.65 | 0 | 2015 | 3 | 0
R80721 | 2015-04-01 | 214.728 |  | 217.411 | 6.307 | 1.752 | 0 | 2015 | 4 | 0
R80721 | 2015-05-01 | 210.024 |  | 218.786 | 6.802 | 1.323 | 0 | 2015 | 5 | 0
R80721 | 2015-06-01 | 164.329 |  | 167.778 | 0.081 | 1.716 | 0 | 2015 | 6 | 0
R80721 | 2015-07-01 | 214.617 |  | 229.916 | 0.263 | 4.058 | 0 | 2015 | 7 | 0.202
R80721 | 2015-08-01 | 162.107 |  | 170.334 | 0.109 | 2.342 | 0 | 2015 | 8 | 0
R80721 | 2015-09-01 | 310.404 |  | 303.52 | 0.073 | 0.893 | 0 | 2015 | 9 | 0.144
R80721 | 2015-10-01 | 128.245 |  | 125.406 | 0.039 | 1.325 | 0 | 2015 | 10 | 0
R80721 | 2015-11-01 | 366.99 |  | 366.884 | 0.392 | 1.2 | 0 | 2015 | 11 | 0.044
R80721 | 2015-12-01 | 283.785 |  | 271.771 | 0.15 | 0.807 | 0 | 2015 | 12 | 0
R80736 | 2014-01-01 | 329.21 |  | 321.27 | 0.017 | 0.079 | 0 | 2014 | 1 | 0
R80736 | 2014-02-01 | 469.853 |  | 467.747 | 3.38 | 0.228 | 0.043 | 2014 | 2 | 0
R80736 | 2014-03-01 | 193.973 |  | 193.143 | 0.019 | 0.693 | 0 | 2014 | 3 | 0
R80736 | 2014-04-01 | 157.237 |  | 159.856 | 0.012 | 0.711 | 0 | 2014 | 4 | 0
R80736 | 2014-05-01 | 280.651 |  | 292.199 | 7.875 | 1.045 | 0 | 2014 | 5 | 0.052
R80736 | 2014-06-01 | 173.086 |  | 188.982 | 2.977 | 3.792 | 0 | 2014 | 6 | 0.296
R80736 | 2014-07-01 | 152.231 |  | 162.636 | 0.093 | 2.225 | 0 | 2014 | 7 | 0.29
R80736 | 2014-08-01 | 151.875 |  | 169.295 | 8.852 | 1.538 | 0 | 2014 | 8 | 0
R80736 | 2014-09-01 | 114.344 |  | 123.053 | 0.027 | 2.23 | 0 | 2014 | 9 | 0
R80736 | 2014-10-01 | 176.785 |  | 179.178 | 0.174 | 1.29 | 0 | 2014 | 10 | 0.037
R80736 | 2014-11-01 | 158.611 |  | 153.018 | 0.056 | 0.395 | 0 | 2014 | 11 | 0
R80736 | 2014-12-01 | 382.251 |  | 377.094 | 2.879 | 0.555 | 0.363 | 2014 | 12 | 0
R80736 | 2015-01-01 | 419.532 |  | 421.753 | 3.071 | 1.086 | 0.345 | 2015 | 1 | 0
R80736 | 2015-02-01 | 288.866 |  | 276.758 | 1.961 | 0.765 | 0.038 | 2015 | 2 | 0
R80736 | 2015-03-01 | 322.976 |  | 320.05 | 0.018 | 0.764 | 0 | 2015 | 3 | 0
R80736 | 2015-04-01 | 225.665 |  | 224.996 | 1.594 | 0.918 | 0 | 2015 | 4 | 0
R80736 | 2015-05-01 | 215.276 |  | 232.184 | 16.167 | 0.68 | 0 | 2015 | 5 | 0
R80736 | 2015-06-01 | 167.727 |  | 173.348 | 0.105 | 1.827 | 0 | 2015 | 6 | 0
R80736 | 2015-07-01 | 230.377 |  | 247.425 | 0.212 | 4.909 | 0 | 2015 | 7 | 0.238
R80736 | 2015-08-01 | 169.945 |  | 182.689 | 2.478 | 2.954 | 0 | 2015 | 8 | 0
R80736 | 2015-09-01 | 323.156 |  | 320.217 | 0.028 | 0.796 | 0 | 2015 | 9 | 0.191
R80736 | 2015-10-01 | 128.85 |  | 127.202 | 0.082 | 0.715 | 0 | 2015 | 10 | 0
R80736 | 2015-11-01 | 403.946 |  | 407.065 | 6.479 | 0.922 | 0.075 | 2015 | 11 | 0
R80736 | 2015-12-01 | 311.581 |  | 296.409 | 0.192 | 0.535 | 0 | 2015 | 12 | 0
R80790 | 2014-01-01 | 313.001 |  | 320.876 | 8.261 | 0.64 | 0.021 | 2014 | 1 | 0
R80790 | 2014-02-01 | 443.942 |  | 444.346 | 0 | 0.66 | 0.053 | 2014 | 2 | 0
R80790 | 2014-03-01 | 216.693 |  | 212.329 | 0.021 | 0.85 | 0 | 2014 | 3 | 0
R80790 | 2014-04-01 | 165.974 |  | 170.414 | 2.167 | 1.067 | 0 | 2014 | 4 | 0
R80790 | 2014-05-01 | 309.447 |  | 312.66 | 0.709 | 1.855 | 0 | 2014 | 5 | 0.042
R80790 | 2014-06-01 | 173.543 |  | 205.117 | 22.928 | 2.967 | 0 | 2014 | 6 | 0.297
R80790 | 2014-07-01 | 167.644 |  | 176.347 | 0.093 | 2.711 | 0 | 2014 | 7 | 0.098
R80790 | 2014-08-01 | 182.279 |  | 187.524 | 0.016 | 1.432 | 0 | 2014 | 8 | 0
R80790 | 2014-09-01 | 130.31 |  | 136.669 | 1.744 | 2.058 | 0 | 2014 | 9 | 0
R80790 | 2014-10-01 | 183.255 |  | 187.927 | 3.356 | 0.891 | 0 | 2014 | 10 | 0.162
R80790 | 2014-11-01 | 161.958 |  | 166.4 | 3.992 | 2.61 | 0.008 | 2014 | 11 | 0
R80790 | 2014-12-01 | 407.118 |  | 412.119 | 0.755 | 2.63 | 1.679 | 2014 | 12 | 0
R80790 | 2015-01-01 | 432.076 |  | 438.497 | 4.127 | 1.964 | 0.862 | 2015 | 1 | 0
R80790 | 2015-02-01 | 268.853 |  | 292.056 | 32.52 | 2.773 | 0 | 2015 | 2 | 0
R80790 | 2015-03-01 | 350.143 |  | 349.73 | 0.544 | 2.66 | 0 | 2015 | 3 | 0
R80790 | 2015-04-01 | 252.369 |  | 254.89 | 3.952 | 3.094 | 0 | 2015 | 4 | 0
R80790 | 2015-05-01 | 250.712 |  | 256.686 | 2.297 | 3.457 | 0 | 2015 | 5 | 0
R80790 | 2015-06-01 | 187.535 |  | 197.614 | 6.204 | 2.961 | 0 | 2015 | 6 | 0
R80790 | 2015-07-01 | 244.315 |  | 262.625 | 1.031 | 6.942 | 0 | 2015 | 7 | 0.225
R80790 | 2015-08-01 | 180.64 |  | 195.557 | 5.177 | 4.02 | 0 | 2015 | 8 | 0
R80790 | 2015-09-01 | 337.757 |  | 343.168 | 3.781 | 3.534 | 0 | 2015 | 9 | 0.218
R80790 | 2015-10-01 | 156.491 |  | 154.551 | 0.07 | 1.949 | 0 | 2015 | 10 | 0
R80790 | 2015-11-01 | 429.873 |  | 435.623 | 1.908 | 2.66 | 0 | 2015 | 11 | 0.055
R80790 | 2015-12-01 | 347.505 |  | 340.837 | 0.033 | 3.116 | 0 | 2015 | 12 | 0

## Fleet_2015
Fleet budget vs actual by month, 2015
Losses shown negative. Check column must be zero: resource + losses + other = variance to budget.
Month no. | Month | Budget MWh | Potential MWh | Wind resource var. | Downtime | Underperf. | Icing | Curtailment | Actual MWh | Other | Variance to budget | Check | Budget revenue | Actual revenue | Revenue variance
1 | Jan | 1821.4528 | 1708.657 | -112.7958 | -12.602 | -7.922 | -2.806 | 0 | 1697.069 | 11.742 | -124.3838 | 0 | 149359.1335 | 139159.658 | -10199.4755
2 | Feb | 1672.2152 | 1153.22 | -518.9952 | -35.056 | -5.385 | -0.385 | 0 | 1178.683 | 66.289 | -493.5322 | 0 | 137121.6442 | 96652.006 | -40469.6382
3 | Mar | 1375.7451 | 1276.401 | -99.3441 | -0.808 | -5.194 | -0.031 | 0 | 1289.368 | 19 | -86.3771 | 0 | 112811.0942 | 105728.176 | -7082.9182
4 | Apr | 915.0486 | 964.139 | 49.0904 | -20.621 | -7.5 | 0 | 0 | 959.749 | 23.731 | 44.7004 | 0 | 75033.9862 | 78699.418 | 3665.4318
5 | May | 672.7786 | 977.815 | 305.0364 | -27.95 | -7.078 | 0 | 0 | 947.7 | 4.913 | 274.9214 | 0 | 55167.8425 | 77711.4 | 22543.5575
6 | Jun | 466.552 | 749.331 | 282.779 | -6.471 | -8.645 | 0 | 0 | 730.56 | -3.655 | 264.008 | 0 | 38257.2669 | 59905.92 | 21648.6531
7 | Jul | 546.2808 | 1017.266 | 470.9852 | -43.725 | -19.17 | 0 | -0.875 | 914.547 | -38.949 | 368.2662 | 0 | 44795.0279 | 74992.854 | 30197.8261
8 | Aug | 441.9838 | 760.002 | 318.0182 | -8.313 | -11.908 | 0 | 0 | 719.857 | -19.924 | 277.8732 | 0 | 36242.672 | 59028.274 | 22785.602
9 | Sep | 656.147 | 1326.324 | 670.177 | -4.259 | -6.589 | 0 | -0.838 | 1341.162 | 26.524 | 685.015 | 0 | 53804.053 | 109975.284 | 56171.231
10 | Oct | 1234.8569 | 575.6 | -659.2569 | -0.487 | -5.464 | 0 | 0 | 590.739 | 21.09 | -644.1179 | 0 | 101258.2632 | 48440.598 | -52817.6652
11 | Nov | 1437.5448 | 1667.979 | 230.4342 | -10.33 | -5.951 | -0.075 | -0.144 | 1665.998 | 14.519 | 228.4532 | 0 | 117878.6708 | 136611.836 | 18733.1652
12 | Dec | 2095.916 | 1302.685 | -793.231 | -0.489 | -5.889 | 0 | 0 | 1363.66 | 67.353 | -732.256 | 0 | 171865.115 | 111820.12 | -60044.995
| 2015 | 13336.5216 | 13479.419 | 142.8974 | -171.111 | -96.695 | -3.297 | -1.857 | 13399.092 | 192.633 | 62.5704 | 0 | 1093594.7695 | 1098725.544 | 5130.7745
Variance to budget, % |  | 0.4692%
Reading: the wind resource column is what the weather did; downtime to curtailment are what operations lost; other is curve scatter and records excluded by data quality.

## Bridge
2015 revenue bridge: budget to actual
Each step links to Fleet_2015 totals; euros = MWh x tariff
Step | MWh | € | Share of budget
Budget | 13336.5216 | 1093594.7695 | 100%
Wind resource | 142.8974 | 11717.5885 | 1.071%
Downtime | -171.111 | -14031.102 | -1.283%
Underperformance | -96.695 | -7928.99 | -0.725%
Icing | -3.297 | -270.354 | -0.02472%
Curtailment | -1.857 | -152.274 | -0.01392%
Other | 192.633 | 15795.906 | 1.444%
Actual | 13399.092 | 1098725.544 | 100.5%
Check: budget + steps - actual | 0
Operational losses, € (downtime to curtailment) |  | -22382.72
Largest operational driver |  | Downtime

## Turbine_2015
Turbine ranking by lost energy and lost revenue, 2015
Rank 1 = most lost energy; act on it first
Turbine | Actual MWh | Potential MWh | Downtime | Underperf. | Icing | Curtailment | Total lost MWh | Lost revenue | Share of fleet loss | Rank | Underperf. 2014 | Underperf. change
R80711 | 3801.926 | 3771.809 | 57.806 | 20.82 | 1.197 | 0.54 | 80.363 | 6589.766 | 29.44% | 2 | 21.829 | -1.009
R80721 | 2951 | 2955.68 | 19.274 | 19.874 | 0.78 | 0.39 | 40.318 | 3306.076 | 14.77% | 4 | 14.342 | 5.532
R80736 | 3207.897 | 3230.096 | 32.387 | 16.871 | 0.458 | 0.429 | 50.145 | 4111.89 | 18.37% | 3 | 14.781 | 2.09
R80790 | 3438.269 | 3521.834 | 61.644 | 39.13 | 0.862 | 0.498 | 102.134 | 8374.988 | 37.42% | 1 | 20.371 | 18.759
Fleet | 13399.092 | 13479.419 | 171.111 | 96.695 | 3.297 | 1.857 | 272.96 | 22382.72 |  |  | 71.323 | 25.372

## Reforecast
Full-year 2015 reforecast
Actuals through the month set on Inputs!B6, budget for the rest of the year
Line | MWh | € | Note
Months of actuals | 6 |  | Set on Inputs
YTD budget | 6923.7923 | 567750.9676
YTD actual | 6803.129 | 557856.578
YTD potential | 6829.563 | 560024.166 | Energy the turbines could have made in the actual wind
YTD operating ratio | 99.61% |  | Actual / potential: share of available wind energy converted
Rest-of-year budget | 6412.7293 | 525843.8019
Reforecast A: YTD actual + budget | 13215.8583 | 1083700.3799 | Assumes rest of year at budget
Reforecast B: YTD actual + budget x operating ratio | 13191.0377 | 1081665.0879 | Carries YTD operational losses forward; normal wind assumed
Full-year budget | 13336.5216 | 1093594.7695
Full-year actual (for back-test) | 13399.092 | 1098725.544 | Known here because 2015 is historical
Error, reforecast A vs actual | -183.2337 | -15025.1641
Error, reforecast B vs actual | -208.0543 | -17060.4561